## NREL (hidden)
Inputs & Assumptions
Site Related
Location | Nepal | # |  |  |  | References |  |  |  |  | Cost Components
Avg. Max Upper Reservoir Depth | 218.1759 | feet | 66.5 | meters | 53 m to 80 m | https://www.researchgate.net/profile/Tej-Saund/publication/291630115_Fish_and_Benthic_Fauna_in_Kulekhani_Reservoir_Makwanpur/links/56a465a408aef91c8c12fafa/Fish-and-Benthic-Fauna-in-Kulekhani-Reservoir-Makwanpur.pdf | 3.2808 | Unit Conversion Factors and Constants
Upper Reservoir Area | 543.6313 | acres | 2.2 | km^2 |  | Adapting hydropower production to climate change_ A case study of Kulekhani Hydropower Project in Nepal.pdf |  | Meter to Feet | 3.2808 | feet | Land and Land Rights
Avg. Max Lower Reservoir Depth | 4133.8584 | feet | 1260 | meters | 10 m | 1015 IOEGC-12-142-12202.pdf |  | Feet to Miles | 0.00018939 | miles
Lower Reservoir Area | 60.2937 | acres | 0.244 | km^2 | 0.244 km^2 | 1016 IOEGC-12-142-12202.pdf |  | Ac. Ft to Cu. Ft | 43559.9 | cu.ft | Powerplant Structure
Nominal (Max) Head | 410.105 | feet | 125 | m |  | 1017 IOEGC-12-142-12202.pdf |  | Cu. Ft to Cu. Yd | 1613.33 | CY
Total Conveyance Length (vert+horiz) | 7217.848 | feet | 2200 | m |  | GIS |  | Hr to Sec | 3600 | s | Reservoirs, Dams, and Waterways
Avg. Upper Dam Height | 374.0158 | ft | 114 | m |  | Adapting hydropower production to climate change_ A case study of Kulekhani Hydropower Project in Nepal.pdf |  | MW to W | 1000000 | W | Upper Reservoir Dam and Spillway
Upper Dam Crest Length | 1332.021 | ft | 406 | m |  | Adapting hydropower production to climate change_ A case study of Kulekhani Hydropower Project in Nepal.pdf |  | acceleration of gravity (metric) | 9.81 | m/s^2 | Upper Reservoir Intake/Outlet
Avg. Lower Dam Height | 118.1102 | ft | 36 | m |  | 1017 IOEGC-12-142-12202.pdf |  | density of water (metric) | 1000 | kg/m^2 | Surge Facilities
Lower Dam Crest Length | 410.105 | ft | 125 | m | taken as dam width | 1018 IOEGC-12-142-12202.pdf |  | sq. km to acres | 247.1051 | acres | Lower Reservoir Intake/Outlet
Acreage to be acquired | 78.3818 | acres | 0.3172 | km^2 | 30% larger than Resovior area |  |  | km to miles | 0.62137 | miles | Lower Reservoir Dam and Spillway
Generation Time | 5 | hours | 6 | hours
Water Conductors
Unit Conversion Factors and Constants | [10 empty] | Upper Low & High Pressure Tunnels
Meter to Feet | 3.2808 | feet | [8 empty] | Vertical Shafts
Feet to Miles | 0.00018939 | miles | [8 empty] | Penstock Tunnels
Ac. Ft to Cu. Ft | 43559.9 | cu.ft | [8 empty] | Draft Tube Tunnels
Cu. Ft to Cu. Yd | 1613.33 | CY | [8 empty] | Tailrace Tunnels
Hr to Sec | 3600 | s | [8 empty] | Surface Penstock
MW to W | 1000000 | W
acceleration of gravity (metric) | 9.81 | m/s^2 | [8 empty] | Powerstation Equipment
density of water (metric) | 1000 | kg/m^2 | [8 empty] | Pump/Motors
Generator/Turbines
Condition Related | [10 empty] | Total Powerstation
Tunneling Condition | Average | #
Access Road, Terrain | Steep | # | [8 empty] | Roads, Railroads, Bridges, and Access
Access Road, Type | New | # | [8 empty] | Access Roads
Highway Realignment | No | # | [8 empty] | Access Tunnels
Access Road | 0 | miles | [8 empty] | Highway Realignment
Access Tunnel, Length | 1.25 | miles
Water Supply = | No | # | [8 empty] | Switchyard
Water Supply Cost = | 0 | $/kW
Transmission Lines
Technology Related
U. Reservoir Intake/Outlet | Horizontal | # | [8 empty] | Others
L. Reservoir Intake/Outlet | Horizontal | # | [8 empty] | Water Supply
Power Station Structure Geology | Adverse | #
Power Station | Underground | # | [8 empty] | Indirect Costs
Penstock | Underground | # | [8 empty] | Mobilization/Demobilization
Sales Tax
Project Related | [10 empty] | Contingency
Inflation Factor | Yes | # | [8 empty] | EPC Cost
Mobilization/Demobilization = | 5% | % | [8 empty] | Developer Cost
Material/Equipment % = | 100% | % | [8 empty] | Overhead & Profit
Sales Tax = | 6% | %
Contingency = | 33% | %
EPC Cost = | 25% | %
Developer Cost = | 3% | %
Overhead & Profit = | 7% | %
Transmission Related
Transmission Distance = | 3.1069 | miles | 5 | km
Transmission = | 230 | kV
Substation = | 230 | kV
Transmission Terrain = | Mountain | #
Transmission Type (# circuits) = | Double | #
Project Related
Active Storage = | 85% | x Gross Storage
Hmin/Hmax = | 0.7 | #
Hazen Williams C = | 90 | #
P-T Efficiency = | 88% | %
Max Tunnel Velocity = | 23 | fps
Max Tunnel Dia = | 35 | feet
Max Unit Capacity = | 50 | MW
Min No. Units = | 2 | #
Pump Time = | 1.2 | x gen time
Output Specifications
Project Related
Conveyance Length | 1.367 | miles
Avg. Upper Reservoir Volume = | 118607.2293 | ac-ft
Avg. Lower Reservoir Volume = | 249245.4311 | ac-ft
Total Upper Dam Volume = | 18807154.6521 | CY
Total Lower Dam Volume = | 732788.9536 | CY
Active Storage = | 100816.1449 | ac-ft
Energy Storage = | 28978.3144 | MWh | 28978.3144
Mean Gen Discharge = | 243974.5105 | cfs
Min Gross Head = | 287.0735 | feet
Mean Gross Head = | 348.5892 | feet
Min Gen Discharge = | 221403.2606 | cfs
Max Gen Discharge = | 264627.5113 | cfs
Nominal Tunnel Dia = | 121.0343 | feet
No. Tunnels = | 2 | #
Adjusted Tunnel Dia = | 85.5842 | feet
L/H = | 20.7059 | #
Surge Chambers | Yes | #
Min Gen Headloss = | 24.8745 | feet
Mean Gen Headloss = | 29.7681 | feet
Max Gen Headloss = | 34.597 | feet
Net Head @ Min Gen Discharge = | 262.199 | feet
Net Head @ Mean Gen Discharge = | 318.8212 | feet
Net Head @ Max Gen Discharge = | 375.508 | feet
Min Plant Gen Power (Firm Capacity) = | 4325.4031 | MW
Mean Plant Gen Power = | 5795.6629 | MW
Max Plant Gen Power = | 2206043.8225 | MW
No. Units = | 63030 | #
Unit Rating = | 34.9999 | MW
Max Penstock Velocity = | 19.5468 | fps
Max Draft Tube Tunnel Velocity = | 8.0819 | fps
Penstock Dia = | 0.52295 | feet
Draft Tube Tunnel Dia = | 0.81328 | feet
Pump Time = | 6 | hrs
Mean Pump Discharge = | 203312.0921 | cfs
Mean Pump Headloss = | 21.2454 | feet
Mean Pump Net Head = | 369.8347 | feet
Mean Pump Power = | 5602.5055 | MW
Tranmission Terrain Multiplier = | 1.75 | #
Tranmission Type Multiplier = | 1 | #

## Plant Output charac (hidden)
Project Related
Conveyance Length | 1.367 | miles | 2199.9953 |  | Unit Conversion Factors and Constants
Avg. Upper Reservoir Volume = | 118606.9428 | ac-ft | 1233.4806 |  | Meter to Feet | 3.2808 | feet
Avg. Lower Reservoir Volume = | 882.2851 | ac-ft | 1088281.572 |  | Feet to Miles | 0.00018939 | miles
Total Upper Dam Volume = | 18807154.6521 | CY | 14379104.125 |  | Ac. Ft to Cu. Ft | 43559.9 | cu.ft
Total Lower Dam Volume = | 732788.9536 | CY | 560257.4584 |  | Cu. Ft to Cu. Yd | 1613.33 | CY
Active Storage = | 2075.6215 | ac-ft | 2560238.874 | m^3 | Hr to Sec | 3600 | s
Energy Storage = | 610.4676 | MWh |  |  | MW to W | 1000000 | W
Mean Gen Discharge = | 4185.8271 | cfs | 118.5294 |  | acceleration of gravity (metric) | 9.81 | m/s^2
Min Gross Head = | 410.105 | feet | 125 |  | density of water (metric) | 1000 | kg/m^2
Mean Gross Head = | 410.105 | feet | 125 |  | cubic meter/second to cfs | 35.3147 | cfs
Min Gen Discharge = | 4185.8271 | cfs | 118.5294 |  | sq feet to acers | 2.2957e-05 | acers
Max Gen Discharge = | 4185.8271 | cfs | 118.5294 |  | cu m to acer foot | 0.00081071 | ac foot
Nominal Tunnel Dia = | 15.2224 | feet | 4.6398
No. Tunnels = | 1 | # |  |  | Unit Conversion Factors and Constants
Adjusted Tunnel Dia = | 15.2224 | feet | 4.6398 |  | Feet to meter | 0.3048
L/H = | 17.6 | # |  |  | Miles to Feet | 5279.9983
Surge Chambers | Yes | # |  |  | Cu feet to Acer feet | 2.2957e-05
Min Gen Headloss = | 72.3651 | feet | 22.0569 |  | Cu Yd to cubic feet | 0.00061984
Mean Gen Headloss = | 72.3651 | feet | 22.0569 |  | sec to hour | 0.00027778
Max Gen Headloss = | 72.3651 | feet | 22.0569 |  | W to MW | 1e-06
Net Head @ Min Gen Discharge = | 337.7399 | feet | 102.9431 |  | acceleration of gravity (metric) | 9.81
Net Head @ Mean Gen Discharge = | 337.7399 | feet | 102.9431 |  | density of water (metric) | 1000
Net Head @ Max Gen Discharge = | 337.7399 | feet | 102.9431 |  | cfs to cubic meter/second | 0.028317
Min Plant Gen Power (Firm Capacity) = | 101.7446 | MW |  |  | acers to sq feet | 43560.0781
Mean Plant Gen Power = | 101.7446 | MW |  |  | acer foot to cu m | 1233.4806
Max Plant Gen Power = | 101.7446 | MW |  |  | miles to meter | 1609.34 | meter
No. Units = | 2 | # |  |  | CY to cu m | 0.76455
Unit Rating = | 50.8723 | MW
Max Penstock Velocity = | 19.5468 | fps | 5.9579
Max Draft Tube Tunnel Velocity = | 7.516 | fps | 2.2909
Penstock Dia = | 11.676 | feet | 3.5588
Draft Tube Tunnel Dia = | 18.8294 | feet | 5.7392
Pump Time = | 6 | hrs
Mean Pump Discharge = | 4185.8271 | cfs | 118.5294
Mean Pump Headloss = | 72.3651 | feet | 22.0569
Mean Pump Net Head = | 482.4701 | feet | 147.0569
Mean Pump Power = | 145.3448 | MW
Tranmission Terrain Multiplier = | 1.75 | #
Tranmission Type Multiplier = | 1.6005 | #

## Plant Specifications
Project Related
Avg. Upper Reservoir Volume = | 118606.9428 | ac-ft | 1233.4806 | m | 1233.48 | 1233.48 m | 1233.48 m
Avg. Lower Reservoir Volume = | 882.2851 | ac-ft | 1088281.572 | m3 | 1088281.57 | 1088281.57 m3 | 1088281.57 m3
Total Upper Dam Volume = | 18807154.6521 | CY | 14379104.125 | m3 | 14379104.12 | 14379104.12 m3 | 14379104.12 m3
Total Lower Dam Volume = | 732788.9536 | CY | 560257.4584 | m3 | 560257.45 | 560257.45 m3 | 560257.45 m3
Active Storage = | 2075.6215 | ac-ft | 2560238.874 | m3 | 2560238.87 | 2560238.87 m3 | 2560238.87 m3
Energy Storage = | 610.4676 | MWh | 610.4676 | MWh | 610.46 | 610.46 MWh | 610.46 MWh
Mean Gen Discharge = | 4185.8271 | cfs | 118.5294 | m3/s | 118.52 | 118.52 m3/s | 118.52 m3/s
Mean Gross Head = | 410.105 | feet | 125 | m | 125 | 125 m | 125 m
Nominal Tunnel Dia = | 15.2224 | feet | 4.6398 | m | 4.63 | 4.63 m | 4.63 m
No. Tunnels = | 1 | # | 1 |  | 1 | 1 | 1
Adjusted Tunnel Dia = | 15.2224 | feet | 4.6398 | m | 4.63 | 4.63 m | 4.63 m
L/H = | 17.6 | # | 17.6 |  | 17.6 | 17.6 | 17.6
Mean Gen Headloss = | 72.3651 | feet | 22.0569 | m | 22.05 | 22.05 m | 22.05 m
Net Head @ Mean Gen Discharge = | 337.7399 | feet | 102.9431 | m | 102.94 | 102.94 m | 102.94 m
Min Plant Gen Power (Firm Capacity) = | 101.7446 | MW | 101.7446 |  | 101.74 | 101.74 | 101.74
No. Units = | 2 | # | 2 |  | 2 | 2 | 2
Unit Rating = | 50.8723 | MW | 50.87 | MW | 50.87 | 50.87 MW | 50.87 MW
Max Penstock Velocity = | 19.5468 | fps | 5.9579 | m/s | 5.95 | 5.95 m/s | 5.95 m/s
Max Draft Tube Tunnel Velocity = | 7.516 | fps | 2.2909 | m/s | 2.29 | 2.29 m/s | 2.29 m/s
Penstock Dia = | 11.676 | feet | 3.5588 | m | 3.55 | 3.55 m | 3.55 m
Draft Tube Tunnel Dia = | 18.8294 | feet | 5.7392 | m | 5.73 | 5.73 m | 5.73 m
Pump Time = | 6 | hrs | 6 | hr | 6 | 6 hr | 6 hr

## NEA Tariff
Poush to Chaitra | Dry season tariff
Peak Time | Normal Time | Peak Time Average | 9.6396
10 | 8.2 | Normal Time Average | 7.6542
10.1 | 8.3
10.2 | 8.4
12.3 | 10.8
13.2 | 12
6.3 | 3
6.2 | 4.6
10.2 | 8.4
7 | 5.5
9.35 | 8.4
8.4 | 4.2
10.5 | 8.55
12.6 | 11.1
13.5 | 12.25
6.4 | 3.1
6.3 | 4.7
10.5 | 8.5
7.15 | 5.6
9.65 | 8.5
8.8 | 4.4
11.3 | 9.1
14.4 | 11.75
7.25 | 5.75
9.75 | 8.6

## Plant Sizing based on NREL (hidden)
Project Related
Conveyance Length | 1.367 | miles
Avg. Upper Reservoir Volume = | 13154.62 | ac-ft
Avg. Lower Reservoir Volume = | 249245.4311 | ac-ft
Total Upper Dam Volume = | 18807154.6521 | CY
|  |  | Total Lower Dam Volume = | 732788.9536 | CY | 0.76455 | m^3 | 560257.4584 | m^3
|  |  | Active Storage = | 1181.427 | ac-ft | 1233.482 | m^3 | 1457268.9141 | m^3
Min Gross Head = | 287.0735 | feet | Energy Storage = | 2305.5093 | MWh
Mean Gross Head = | 348.5892 | feet | Mean Gen Discharge = | 22549.1593 | cfs | 0.028317 | M63/s | 638.5211 | m
Min Gen Discharge = | 20463.0286 | cfs | L/H = | 20.7059
Max Gen Discharge = | 24457.9973 | cfs | Net Head @ Max Gen Discharge = | 270.7723 | feet | 0.3048 |  | 82.5314 | m
Nominal Tunnel Dia = | 36.7961 | feet | Max Plant Gen Power = | 493.4425 | MW
No. Tunnels = | 2 | # | No. Units = | 2 | #
Adjusted Tunnel Dia = | 26.0188 | feet | Unit Rating = | 246.7212 | MW
#
Surge Chambers | Yes | #
Min Gen Headloss = | 100.1772 | feet | Total Lower Dam Volume = | 560257.4584
Mean Gen Headloss = | 119.8852 | feet | Active Storage = | 1457268.9141
Max Gen Headloss = | 139.3327 | feet | Energy Storage = | 2305.5093
Net Head @ Min Gen Discharge = | 186.8963 | feet | Mean Gen Discharge = | 638.5211
Net Head @ Mean Gen Discharge = | 228.704 | feet | L/H = | 20.7059
|  |  | Net Head @ Max Gen Discharge = | 82.5314
Min Plant Gen Power (Firm Capacity) = | 284.9588 | MW | Max Plant Gen Power = | 493.4425
Mean Plant Gen Power = | 384.2515 | MW | No. Units = | 2
|  |  | Unit Rating = | 246.7212
Max Penstock Velocity = | 19.5468 | fps
Max Draft Tube Tunnel Velocity = | 8.0819 | fps
Penstock Dia = | 28.2236 | feet
Draft Tube Tunnel Dia = | 43.8927 | feet
Pump Time = | 7.2 | hrs
Mean Pump Discharge = | 18790.9661 | cfs
Mean Pump Headloss = | 85.5619 | feet
Mean Pump Net Head = | 434.1511 | feet
Mean Pump Power = | 607.8572 | MW
Tranmission Terrain Multiplier = | 1.75 | #
Tranmission Type Multiplier = | 1.6005 | #

## ENTURA (hidden)
1
Upper reservoir
53364852
1.1
Embankment
45628209
1.2
Liner
7736643
2
Lower reservoir
53364852
2.1
Embankment
45628209
2.2
Liner
7736643
3
Intakes
16137431
4
Waterways
47636431
5
Power Station (E&M)
137313041
6
Power Station (civil)
34328260
7
Access tunnels and construction adits
24000000
8
Access roads to site
2000000
9
Transmission line
16000000
10
Miscellaneous
8082897
11
Sub-total works
412227764
12
Other development costs
267948046
12.1
Preliminaries and general – 20%
82445553
12.2
Design and approvals – 10%
41222776
12.3
Owner’s costs – 5%
20611388
12.4
Contingency – 20%
123668329
13
Total
680175810

## Sheet2 (hidden)
Inputs | Decription | Value
Serial
| Input | Values
1 | Head, H (m) | 125
2 | Waterway length, L (m) | 2200
3 | Storage volume (Mm3) | 3.57
4 | Storage time (hr) | 6
5 | Transmission length (km) | 5
Calculated values
5 | Length: Head Ratio
6 | Flow (m3/s)
7 | Pump/Turbine Efficiency3 | 94%
8 | Motor/Generator Efficiency3 | 98%
9 | Installed Capacity (MW) | 100
10 | Energy in storage (MWh) | 4518
11 | Storage perimeter (m) | 1942
12 | Embankment volume (m3) | 912564
13 | Embankment liner area (m2) | 386832
14 | Waterway diameter (m) | 5.8
15 | Access road length (km) | 4

## Sheet3 (hidden)
Inputs
Serial | Decription | Value
Input Values
1 | Head, H (m) | 400
2 | Waterway length, L (m) | 1500
3 | Storage volume (Mm3) | 4.5
4 | Storage time (hr) | 12
5 | Transmission length (km) | 20
Calculated values
5 | Length: Head Ratio | 3.8
6 | Flow (m3/s) | 104
7 | Pump/Turbine Efficiency3 | 94%
8 | Motor/Generator Efficiency3 | 98%
9 | Installed Capacity (MW) | 377
10 | Energy in storage (MWh) | 4518
11 | Storage perimeter (m) | 1942
12 | Embankment volume (m3) | 912564
13 | Embankment liner area (m2) | 386832
14 | Waterway diameter (m) | 5.8
15 | Access road length (km) | 4

## Costing Entura (hidden)
Reference Plant Size (MW) | 337
CPI in 2018 | 251.23 | Reference Site
CPI in 2025 | 323.976 | Reference Site
Size of Kulekhani_Sisneri PSH (MW) | 100
Cost Estimate
Description | Amount (2018) | Amount (2025) | $/kWh (2025) | Estimated Cost for KS PSH
Upper reservoir | 53364852 | 68817144.8137 | 204.2052 | 20420517.7489
Embankment | 45628209 | 58840284.3569 | 174.6003 | 17460025.0317
Liner | 7736643 | 9976860.4568 | 29.6049 | 2960492.7172
Lower reservoir | 53364852 | 68817144.8137 | 204.2052 | 20420517.7489
Embankment | 45628209 | 58840284.3569 | 174.6003 | 17460025.0317
Liner | 7736643 | 9976860.4568 | 29.6049 | 2960492.7172
Intakes | 16137431 | 20810175.32 | 61.7513 | 6175126.2077
Waterways | 47636431 | 61430005.8498 | 182.2849 | 18228488.3827
Power Station (E&M) | 137313041 | 177073318.3577 | 525.4401 | 52544011.3821
Power Station (civil) | 34328260 | 44268329.267 | 131.36 | 13136002.7499
Access tunnels and construction adits | 24000000 | 30949424.8298 | 91.8381 | 9183805.5875
Access roads to site | 2000000 | 2579118.7358 | 7.6532 | 765317.1323
Transmission line | 16000000 | 20632949.8866 | 61.2254 | 6122537.0583
Miscellaneous | 8082897 | 10423375.5462 | 30.9299 | 3092989.7763
Sub-total works | 412227764 | 531592174.7787 | 1577.4249 | 157742485.0976
Other development costs | 267948046 | 345534912.8324 | 1025.3262 | 102532615.0838
Preliminaries and general - 20% | 82445553 | 106318435.2137 | 315.485 | 31548497.096
Design and approvals - 10% | 41222776 | 53159216.9621 | 157.7425 | 15774248.3567
Owner's costs - 5% | 20611388 | 26579608.481 | 78.8712 | 7887124.1783
Contingency - 20% | 123668329 | 159477652.1757 | 473.2275 | 47322745.4527
Total | 680175810 | 877127087.6112 | 2602.751 | 260275100.1814

## Black & (hidden)
Reference Plant Size (MW) | 500
CAPEX (2025) $/kWh | 2230
Size of Kulekhani_Sisneri PSH (MW) | 100
Description | $/kW (2025) | % of CAPEX | Estimated Cost for KS PSH
Upper Resovior | 423.7 | 0.19 | 42.37
Tunnels | 133.8 | 0.06 | 13.38
Power House excavation | 89.2 | 0.04 | 8.92
Power House | 825.1 | 0.37 | 82.51
Engineering procurement, Construction management services | 379.1 | 0.17 | 37.91
Owners Cost | 379.1 | 0.17 | 37.91

## NREL Direct (hidden)
Reference Plant Size (MW) | 116.2 | MW
CPI in 2018 | 292.656 | Reference Site
CPI in 2025 | 323.976 | Reference Site
| Price ($) | Price ($) 2025 | $/kW
Resovior Cost | 11873465 | 13144161.3937 | 113.1167
WaterWays | 50682448 | 56106475.771 | 482.844 |  | 35263107 | 303.4691
Powerouse Civil | 21802721 | 24136044.84 | 207.7112
Electrical and Mechanical Cost | 73985792 | 81903740.0531 | 704.8515 |  | 15862782
Engineering Procuremnt and Construction cost | 69282995.3816 | 76697650.8657 | 660.0486 |  | 55644499
Owner Cost | 216913259 | 240127282.5358 | 2066.4998
Reservoirs, Dams, and Waterways |  |  |  | Resovior Cost
|  |  |  | Upper Reservoir Dam and Spillway | 5547274
|  |  |  | Upper Reservoir Intake/Outlet | 1145442
|  |  |  | Lower Reservoir Intake/Outlet | $ -
|  |  |  | Lower Reservoir Dam and Spillway | 5180749
Water Ways
Water Conductors |  |  |  | Surge Facilities | 14480699
|  |  |  | Upper Low & High Pressure Tunnels | 24535083.7487
|  |  |  | Vertical Shafts | 7451689.1976
Penstock Tunnels | 0 |  |  | Surface Penstock | 4214975.6989
Draft Tube Tunnels | 0
Tailrace Tunnels | 0
Electrical and Mechanical Cost
|  |  |  | Pump/Motors | 15862782.0288
Powerstation Equipment |  |  |  | Generator/Turbines | 55644499.1552
|  |  |  | Switchyard | 2478511.0688
Power House Civil
Total Powerstation | 0 |  |  | Plant Structure | 21802721.0968
Draft tube Tunnel
Roads, Railroads, Bridges, and Access
Access Roads | 1641809.0458 |  |  | Engineering Procuremnt and Construction cost
Access Tunnels | 0 |  |  | Mobilization/Demobilization | 13856599.0763
|  |  |  | Sales Tax | 16627918.8916
|  |  |  | Overhead & Profit | 19399238.7069
|  |  |  | EPC Cost | 69282995.3816
Owner Cost
|  |  |  | Land Right | 5954843.4223
|  |  |  | Highway Realiment | 410452.2614
Others |  |  |  | Transmission Lines | 110780450.4175
Water Supply | 0 |  |  | Contingency | 91453553.9038
|  |  |  | Developer Cost | 8313959.4458
Indirect Costs
Total Direct and Indirect Cost | 496066246.9326

## CAPEX Estimation
CAPEX Element | ENTURA | Black and Veatch | NPREL | CAPEX Cost Elements
Lower Reservoir | 204.21 | 423.7 | 113.1167 | 225.6095
Waterways | 182.28 | 120 | 482.844 | 372.276
Powerouse Civil | 131.36 | 70 | 207.7112 | 172.0342
Electrical and Mechanical Cost | 525.44 | 750 | 704.8515 | 682.4743
Engineering Procuremnt and Construction cost | 253.4 | 379.1 | 660.0486 | 404.9748
Owner Cost | 78.87 | 379.1 | 2066.4998 | 460.18 | 2317.5487
Total |  |  |  | 2317.5487